## BoQ
Name: | Water supply, Sanitary drainage and other repair and maintance works 2025
Location | Bhutan Post HQ/GPO building, Thimphu
Sl. No. | Item Description | Quantity | Unit | Rate (Nu.) in figures | Rate (Nu.) in words | Amount (Nu.)
A | EARTHWORK, DISMANTLING & DEMOLITION WORK
A.1 | Excavation in trenches or drains including dressing & ramming, disposal of surplus soil within 50m lead & 1.5m lift | 24.47 | cu.m
A.2 | Demolishing cement concrete 1:3:6 & richer, including disposal of materials within 50m lead | 1.5 | cu.m
A.3 | Demolishing brick work in cement mortar including stacking useful materials & disposal of rubbish within 50m lead | 8.27 | cu.m
A.4 | Dismantling tiled flooring and walls, in cement mortar including stacking useful materials & disposal of rubbish within 50m lead | 132.3 | sq.m
A.5 | Dimsantling laminated partition boards and door shutters, with stainless steel tubular sections clamps, hinges, stands, and all fittings, inlcuding reinstallation of the same | 24.616 | sq.m
A.6 | Dismantling of old CI/PVC SWR soil waste and vent pipes including taking out the pipes, breaking lead caulked joints, stacking of pipes at site and disposal of rubbish within 50m lead, upto 150 mm dia | 202.19 | m
A.7 | Dismantling CI pipes including excavation and refilling trenches after taking out the pipes, breaking lead caulked joints, melting of lead and making into blocks, stacking of pipes at site and disposal of rubbish within 50m lead, upto 300 mm dia | 72.5 | m
Underground sanitary sewage line
A.8 | Dimsantling of Chlorinated Polyvinyl Chloride (CPVC) pipes - for hot & cold water supply, including all faucets, fittings, clamps and stacking of useful materials within 50 m lead. | 225.72 | m
A.9 | Dismantling of flushing cistern of any size including stacking of useful materials & disposal of rubbish within 50 m lead | 45 | no.
B | STONE, SAND & BRICK WORK
B.1 | Providing and laying hand packed stone filling or soling with stones | 0.05 | cu.m
B.2 | Providing & laying sand bedding, including watering, ramming, dressing | 7.51 | cu.m
B.3 | Providing & laying second-class half-brick masonry (125 mm) in superstructure below floor 2 level | 6.11 | sq.m
B.4 | Providing & laying second-class brick work in superstrucure above plinth level, upto floor two level | 8.88 | cu.m
B.5 | Providing and laying filter material (450 mm wide) in trenches, sides of foundations, walls etc. with 100 to 200 mm stones wherever applicable. | 6.53 | cu.m |  |  | 0
C | CONCRETE WORK
C.1 | Providing and laying plain cement concrete 1:2:4 (1cement: 2 coarse sand:4 graded stone aggregate of 20 mm nominal size, excluding the cost of centering and shuttering- All work upto plinth level. | 0.196 | cu.m
D | WATER-PROOFING
D.1 | Providing and laying of liquid rubber water proofing membrance in wet area floors and walls, brand MYK Laticrete 9237 and equivalent | 150 | sq.m
E | WOOD WORK
E.1 | Providing & fixing Panelled partition, single-central-panelling including frame etc. complete. 100mm framing, 38mm thick Class 'A' (conifer) or Class 'A' (conifer) panelling | 3.88 | sq.m
E.2 | Providing & fixing wooden skirting in Class 'B' (conifer) with necessary nails or screws complete - 20 mm thickness | 9.42 | sq.m
E.3 | Providing & fixing in position dressed wood work in frames of doors - Class 'A' (conifer) | 0.059 | cu.m
E.4 | Providing & fixing 35mm thick Panelled doors shutter, complete including hinges - Class 'A' (conifer) | 1.8405 | sq.m
E.5 | Providing & fixing Plywood lining with necessary nails etc. including beading complete (excluding cost of frame) | 2.42 | sq.m
F | STEEL WORK
F.1 | Steel work welded, in built up sections, trusses, frame-works including cutting, hoisting, fixing and appl. priming coat of red lead paint in welded tube (250 MPa) - 40 mm outer dia, section thickness 2.77 mm | 218.48 | kg
F.2 | Providing & fixing anodised Aluminium section for doors and partitions framing of specified sections including all accessories such as U-rubber gasket for fixing glass panes, weather strips or weather seals, etc complete including the cost of 5 mm thick plain glass or 8 mm boards in case of partitions and doors. | 25.27 | sq.m
F.3 | Providing and installation of prefabricated stainless steel wheels & door track roller, channel, hanging type sliding door set
F.3.a | Door | 2 | set |  |  | 0
F.3.b | Swinging partition | 1 | set |  |  | 0
G | TILING WORK
G.1 | Providing and laying tiles in flooring (600 mm x 600 mm x 12 mm) in all colours and shade, laid on 20 mm thick cement mortar 1:4 (1 cement: 4 coarse sand) finished with flush pointing in white cement | 13.17 | sq.m
G.2 | Providing and fixing tiles in wall in different sizes (600mm x 600 mm x 12mm) in all colours and shade, on 12 mm thick cement mortar 1:3 (1 cement:3 sand) finished with flush-pointing in white cement | 37.22
H | Plumbing Work
H.1 | Providing and fixing Chlorinated Polyvinyl Chloride (CPVC) pipes - class 1 (SDR11), having thermal stability for hot & cold water supply, including all CPVC plain & brass threaded fittings, including fixing the pipe with clamps at 1.00 m spacing. This includes jointing of pipes & fittings with one step CPVC solvent cement and testing of joints complete as per direction of Engineer in Charge. Internal work - Exposed on wall. |  | m
H.1.a | 40 mm nomimal outer dia pipes | 50 | m |  |  | 0
H.1.b | 32 mm nomimal outer dia pipes | 75 | m |  |  | 0
H.2 | Providing and fixing Chlorinated Polyvinyl Chloride (CPVC) pipes - class 1 (SDR11), having thermal stability for hot & cold water supply, including all CPVC plain & brass threaded fittings, i/c fixing the pipe with clamps at 1.00 m spacing. This includes jointing of pipes & fittings with one step CPVC solvent cement and the cost of cutting chases and making good the same including testing of joints complete as per direction of Engineer in Charge. Concealed work, including cutting chases and making the good walls etc. |  |  |  |  | 0
H.2.a | 20 mm nomimal outer dia pipes | 100 | m |  |  | 0
H.3 | Providing & fixing white vitreous china wash basin, including C.I brackets, 15mm C.P. brass pillar taps, c.p. chain & rubber plug, 32mm pvc waste, 32mm dia. trap & union, repair walls- Flat back wash basin 630x450mm
H.4 | Providing & fixing European-type vitreous china w.c pedestal including seat and lid with c.p brass hinges, 15 lit white vitreous china low level cistern, fittings, brackets, repair walls | 1 | each |  |  | 6295.1
H.5 | Providing & fixing c.p. brass stop cock - 20mm, standard, c.p knob | 1 | each |  |  | 1217.31
H.6 | Providing & fixing bevelled edge mirror (superior glass) incl.4mm A.C sheet base fixed to wooden cleats
| 400x450mm | 1 | each |  |  | 2052.4
| 2730x730 mm | 1 | each |  |  | 11839.58
H.7 | Providing & fixing toilet paper holder - C.P. brass | 1 | each |  |  | 663.43
New conference hall toilet
H.8 | Providing & fixing soap dish including brackets, wooden cleats, c.p. brass screws | 1 | each |  |  | 549.69
H.9 | Providing & fixing Indian-type vitreous china w.c squatting pan with 10 litres vitreous china cistern including 100 mm P trap, fittings and repairing walls complete | 2 | each |  |  | 0
H.10 | Providing & fixing P.P (Polypropylene) three layered soil waste pipes, single or double socketed, including pipe clip complete (excluding the cost of P.P fittings)- 110 mm dia | 350 | m |  |  | 0
H.11 | Providing & fixing P.V.C vent pipes, single or double socketed, including pipe clip complete (excluding the cost of PVC fittings)- 75 mm dia | 120 | m |  |  | 0
H.12 | Providing & fixing P.P Pipe connector( 100 mm dia) | 36 | each |  |  | 0
H.13 | Providing & fixing P.P Coupler (110 mm dia) | 36 | each |  |  | 0
H.14 | Providing & laying H.D.P.E pipes, 10 PN, including H.D.P.E fittings (excluding trenching, refilling & thrust block)160 mm | 72.5 | m |  |  | 0
H.15 | Providing & fixing P.P nahani floor trap 110 mm x 75 mm | 12 | each |  |  | 0
H.16 | Providing & fixing P.P Coupler 75 mm | 36 | each |  |  | 0
H.17 | Providing & fixing P.P Coupler 110 mm | 18 | each |  |  | 0
H.18 | Providing & fixing P.P Reducer 110x75 mm | 36 | each |  |  | 0
H.19 | Providing & fixing P.P plain bend 75 mm | 18 | each |  |  | 0
H.20 | Providing & fixing P.P plain bend 110 | 20 | each |  |  | 0
H.21 | Providing & fixing P.P Single Y, plain, 110 mm dia | 22 | each |  |  | 0
H.22 | Providing & fixing P.P Double Y, with door 110 mm dia | 8 | each |  |  | 0
H.23 | Providing & fixing P.P single Tee plain, 75 mm dia | 12 | each |  |  | 0
H.24 | Fixing of usable wash basins | 20 | no. |  |  | 0
H.25 | Fixing of water closets & urinals | 25 | no. |  |  | 0
I | PLASTERING AND PAINTING WORK
I.1 | Providing & laying 12mm cement plaster in C.M 1:3, including providing and mixing water-proofing materials in proportion recommended by the manafacturers | 236 | sq.m
I.2 | Finishing wall with water-proof cement paint, new work, 3 coats | 236
I.3 | Providing, preparing and applying Sumdang painting (Not washable), Rab | 7.44 | sq.m
I.4 | Providing and applying finishing coats Synthetic enamel, for steel & wood work, two coats on new work | 2.42 | sq.m
J | ROAD WORKS
J.1 | Consolidation of sub-grade with plate compactor, and making good the undulation with earth and re-compacting the sub grade | 32.625 | sq.m
J.2 | Providing and laying Granular sub-base course (GSB) 220mm to required degree of compaction with proper formation of cross fall using motor grader for laying and compacted to required density as per material gradation and aggregate quality specified | 7.18 | cu.m
J.3 | Providing and laying wet mix macadam graded aggregate base course 100 mm to required degree of compaction with proper formation of cross fall by using well graded crushed aggregates premixed with OMC using suitable mixer, motor grader as per material gradation and aggregates quality specified | 3.26 | cu.m
J.4 | Premix consolidated carpet surfacing including a tack coat @ 0.75 kg bitumen emulsion per sq.m of road surface | 32.63 | sq.m
K | ELECTRICAL WORK
K.1 | Wiring for 5/6 pin, 16 ampere plug point with 4 sq.mm 1.1kV grade,PVC insulated copper conductor cable in PVC casing & capping with providing and fixing 5/6 pin, 6/16 ampere socket outlet & switch including earthing the third pin,connections, painting, testing & commissioning etc. as required, Long point | 1 | point
K.2 | Wiring for light and 2 pin light socket outlet with 1.5 sq.mm 1.1kV grade, PVC insulated copper conductor cable inrecessed HDPE pipe including connections, painting, testing and commissioning etc. as required, medium point | 1 | point
K.3 | Supplying & fixing of prewired indoor recessed mounted round/Square LED luminiares of 3000/4000/6000k, complete with all accessories with necessary testing & commissioning & cutting & painting as required. | 1 | each
| 8W | 1 |  |  |  | 0
K.4 | Providing, installation, testing and commissioning of pressure booster pump rated at 0.5 hp, with automatic mode of operation, single phase, all accessories complete. Brand Grundfos and equivalent | 1 | set |  |  | 0

## Details
Name: | Water supply, Sanitary drainage and other repair and maintance works 2025
Location | Bhutan Post HQ/GPO building, Thimphu
Sl. No. | Item Description | Length (m) | Breadth (m) | Height/ depth (m) | Nos. | Quantity | Unit | Estimated Rates | Amount (Nu.) | BSR reference
A | EARTHWORK, DISMANTLING & DEMOLITION WORK
A.1 | Excavation in trenches or drains including dressing & ramming, disposal of surplus soil within 50m lead & 1.5m lift | [5 empty] | cu.m | 443 |  | EW0106
| Trenching for sanitary line till connection to the existing IC/manholes | 72.5 | 0.45 | 0.75 | 1 | 24.4688 |  |  | 10839.66
A.2 | Demolishing cement concrete 1:3:6 & richer, including disposal of materials within 50m lead | 1 | 1 | 1.5 | 1 | 1.5 | cu.m | 1088.67 | 1633.005
A.3 | Demolishing brick work in cement mortar including stacking useful materials & disposal of rubbish within 50m lead | [5 empty] | cu.m | 751.52 |  | DD0017
Ground floor
| Postal museum toilet | 1 | 1 | 0.12 |  | 0.12
| IMS toilet | 1 | 1 | 0.12 |  | 0.12
| GPO toilet | 2 | 2 | 0.12 |  | 0.48
| 1st floor Ladies toilet | 5.55 | 4.46 | 0.2 |  | 4.95
| deduction | 1.93 | 0.77 | 0.2 |  | 0.3
| Subtotal |  |  |  |  | 4.65
| Gents toilet, 1st floor | 5.6 | 4.2 | 0.08 |  | 1.88
| addition | 1.38 | 2.47 | 0.08 |  | 0.27
| Total quantity for demolishing of brick work |  |  |  |  | 7.52
| Toal quantity with 10% contingency |  |  |  |  | 8.27 | cu.m |  | 6215.0704
A.4 | Dismantling tiled flooring and walls, in cement mortar including stacking useful materials & disposal of rubbish within 50m lead | [5 empty] | sq.m | 73.88 |  | DD0040
| Ladies toilet 1st floor | 5.575 | 5.55 |  |  | 30.94
| Gents toilet 1st floor |  |  |  |  | 22.26
| Toilet next the GAB on first floor stair case landing right side, wall tiles | 4 |  | 1.8 | 2 | 14.4
|  | 2.5 |  | 1.8 | 2 | 9
| Provision for partition walls @ 20 % |  |  |  |  | 4.68
GF-Postal museum toilet
| to access the removal of old cpvc pipe and drainage pipe for all toilets | 48.29 | 0.3 |  | 2 | 28.974
| Subtotal Quantity |  |  |  |  | 110.254
| Contingency 20% | 20% |  |  |  | 22.0508
| Total estimated quantity |  |  |  |  | 132.3 | sq.m |  | 9774.324
A.5 | Dimsantling laminated partition boards and door shutters, with stainless steel tubular sections clamps, hinges, stands, and all fittings, inlcuding reinstallation of the same | [5 empty] | sq.m | 634.21 |  | DD0065, WW0181 (AR3)
| Ladies restroom | 1.72 |  | 1.81 | 5 | 15.566
|  | 5 |  | 1.81 | 1 | 9.05
| Net Quantity |  |  |  |  | 24.616 | sq.m |  | 15611.7134
A.6 | Dismantling of old CI/PVC SWR soil waste and vent pipes including taking out the pipes, breaking lead caulked joints, stacking of pipes at site and disposal of rubbish within 50m lead, upto 150 mm dia | [5 empty] | m | 50 |  | DD0076
| Service duct 1 |  |  | 10.5 | 6 | 63
| Service duct 2 |  |  | 10.5 | 6 | 63
| Service duct 3 |  |  | 7 | 6 | 42
| All toilets | 34.19 |  |  |  | 34.19
| Estimated quantity |  |  |  |  | 202.19 | m |  | 10109.5
A.7 | Dismantling CI pipes including excavation and refilling trenches after taking out the pipes, breaking lead caulked joints, melting of lead and making into blocks, stacking of pipes at site and disposal of rubbish within 50m lead, upto 300 mm dia | [5 empty] | m | 200.84 |  | DD0078, DD0079
| Underground sanitary sewage line | 72.5 | [6 empty] | 14560.9
A.8 | Dimsantling of Chlorinated Polyvinyl Chloride (CPVC) pipes - for hot & cold water supply, including all faucets, fittings, clamps and stacking of useful materials within 50 m lead. | [5 empty] | m | 25 |  | DD0075 (AR2)
| Horizontal pipe | 44.9 |  |  | 3 | 134.7
| Vertical pipe | 8.9 |  |  | 6 | 53.4
| Subtotal |  |  |  |  | 188.1
| Contingency 20% |  |  |  |  | 37.62
| Estimated quantity |  |  |  |  | 225.72 |  |  | 5643
A.9 | Dismantling of flushing cistern of any size including stacking of useful materials & disposal of rubbish within 50 m lead | [5 empty] | no. | 349.58 |  | DD0100
| Ground floor postal museum toilet -Wash closets |  |  |  | 2
| Wash basin |  |  |  | 1
| IMS toilet ground floor -Wash basin |  |  |  | 1
| EWC |  |  |  | 1
| GPO toilet ground floor- Wash basin |  |  |  | 2
| EWC |  |  |  | 2
| First floor ladies toilet-wash basin |  |  |  | 4
| EWC |  |  |  | 6
| Urinals-1st floor gents toilet |  |  |  | 4
| Wash basin-1st floor gents toilet |  |  |  | 4
| EWC- 1st floor gents toilet |  |  |  | 4
| Wash closet- 1st floor toilet next to GAB office |  |  |  | 2
| Wash basin- 1st floor toilet next to GAB office |  |  |  | 1
| Wash basin- IAU |  |  |  | 1
| EWC- IAU |  |  |  | 1
| Wash basin - Philately division |  |  |  | 1
| EWC - Philately division |  |  |  | 1
| Second floor |  |  |  | 7
| Total quantity |  |  |  | 45 | 45 | no. |  | 15731.1
B | STONE, SAND & BRICK WORK
B.1 | Providing and laying hand packed stone filling or soling with stones | [6 empty] | 1230.58 |  | SM0072
| For generator roofing post | 0.3 | 0.3 | 0.15 | 4 | 0.05 | cu.m |  | 61.529
B.2 | Providing & laying sand bedding, including watering, ramming, dressing | [6 empty] | 1596.12 |  | EW0196
| Sand bedding for HDPE pipes | 72.5 | 0.45 | 0.275 |  | 8.97
| Deduction for volume of HDPE pipe (.08 m radius) | 72.5 | 3.14 | 0.08 | 0.08 | 1.46
| Net |  |  |  |  | 7.51 |  |  | 11986.8612
B.3 | Providing & laying second-class half-brick masonry (125 mm) in superstructure below floor 2 level | [5 empty] | sq.m | 1472.27 |  | BW0021
| New conference hall toilet | 2.61 |  | 2.34 | 1 | 6.11 | sq.m |  | 8995.5697
B.4 | Providing & laying second-class brick work in superstrucure above plinth level, upto floor two level | [5 empty] | cu.m | 10679.32 |  | BW0002, BW0012
| New conference hall toilet | 2.61 | 2.34 | 0.1 | 1 | 0.61
| Old toilets repair works |  |  |  |  | 8.27
| Estimated quantity |  |  |  |  | 8.88 | cu.m |  | 94832.3616
B.5 | Providing and laying filter material (450 mm wide) in trenches, sides of foundations, walls etc. with 100 to 200 mm stones wherever applicable. | 72.5 | 0.45 | 0.2 |  | 6.53 | cu.m | 1230.58 | 8035.6874
C | CONCRETE WORK
C.1 | Providing and laying plain cement concrete 1:2:4 (1cement: 2 coarse sand:4 graded stone aggregate of 20 mm nominal size, excluding the cost of centering and shuttering- All work upto plinth level. | [5 empty] | cu.m | 6570.06 |  | CW0003
| PCC for generator roofing post | 0.3 | 0.3 | 0.1 | 4 | 0.036
| Thrust block on HDPE bends | 0.3 | 0.3 | 0.3 | 6 | 0.16
| Sub-total |  |  |  |  | 0.196 | cu.m |  | 1287.73
D | WATER-PROOFING
D.1 | Providing and laying of liquid rubber water proofing membrance in wet area floors and walls, brand MYK Laticrete 9237 and equivalent | [5 empty] | sq.m | 500
| New conference hall toilet floor | 2.64 | 1.2 |  | 1 | 3.17
| New conference hall toilet walls | 2.64 |  | 1.82 | 2 | 9.61
|  | 1.2 |  | 1.82 | 2 | 4.37
| Deductions, door |  | 0.8 | 1.82 | 1 | 1.46
window portion
| Estimated quantity |  |  |  |  | 15.69 | sq.m |  | 7845
E | WOOD WORK
E.1 | Providing & fixing Panelled partition, single-central-panelling including frame etc. complete. 100mm framing, 38mm thick Class 'A' (conifer) or Class 'A' (conifer) panelling | [5 empty] | sq.m | 2660.71 |  | WW0172
| Store next to new conference hall | 2.61 |  | 2.34 | 1 | 7.11 | sq.m
| deduction for door |  | 1.05 | 2.12 | 1 | 3.23 | sq.m
| Estimated quantity |  |  |  | 1 | 3.88 | sq.m |  | 10323.55
E.2 | Providing & fixing wooden skirting in Class 'B' (conifer) with necessary nails or screws complete - 20 mm thickness | [5 empty] | sq.m | 1842.82 |  | WW0150
| New conference hall floor skirting | 55.44 |  | 0.17 |  | 9.42 |  |  | 17359.36
New conference hall, Door and accessories
E.3 | Providing & fixing in position dressed wood work in frames of doors - Class 'A' (conifer) | [5 empty] | cu.m | 26997.9 |  | WW0001
| Store room door next to new conference hall | 0.075 | 0.075 | 2.12 | 2 | 0.02385
|  | 0.075 | 0.075 | 0.9 | 1 | 0.00506
| Big mart area back door | 0.075 | 0.075 | 5.36 | 1 | 0.03015
| Estimated quantity |  |  |  |  | 0.05906 | cu.m | 26997.9 | 1594.496
E.4 | Providing & fixing 35mm thick Panelled doors shutter, complete including hinges - Class 'A' (conifer) | [5 empty] | sq.m | 2565.89 |  | WW0210
| Store room door next to new conference hall |  | 0.9 | 2.045 | 1 | 1.8405 | sq.m |  | 4722.5205
E.5 | Providing & fixing Plywood lining with necessary nails etc. including beading complete (excluding cost of frame) | [5 empty] | sq.m | 670.08
| Big mart area back door | 1.1 |  | 2.2 | 1 | 2.42 | sq.m |  | 1621.5936
F | STEEL WORK
F.1 | Steel work welded, in built up sections, trusses, frame-works including cutting, hoisting, fixing and appl. priming coat of red lead paint in welded tube (250 MPa) - 40 mm outer dia, section thickness 2.77 mm | [5 empty] | kg | 96.48 |  | SW0022
| Horizontal sections | 5.85 |  |  | 2 | 11.7
| Vertical sections | 6.7 |  |  | 2 | 13.4
| Inclined sections | 3.39 |  |  | 2 | 6.78
| Diagonal sections | 12 |  |  | 1 | 12
| Sub-total |  |  |  |  | 43.88 | m
| Unit weight 2.7 kg/m, 2.77 mm minimum section thickness |  |  |  |  | 118.48 | kg
| Re-alignment of pedestrain gate |  |  |  |  | 100 | kg
| Sub-total |  |  |  |  | 218.48 | kg |  | 21078.9504
F.2 | Providing & fixing anodised Aluminium section for doors and partitions framing of specified sections including all accessories such as U-rubber gasket for fixing glass panes, weather strips or weather seals, etc complete including the cost of 5 mm thick plain glass or 8 mm boards in case of partitions and doors. | [5 empty] | sq.m | 2500
| Between Finance Division and Finance Head | 5.05 |  | 3.12 | 1 | 15.756
|  | 3.05 |  | 3.12 | 1 | 9.516
| Total estimated quantity |  |  |  |  | 25.272 | sq.m |  | 63180
| Providing and installation of prefabricated stainless steel wheels & door track roller, channel, hanging type sliding door set | [5 empty] | set
| Door |  |  |  | 2 | 2 | set | 10890 | 21780
| Swinging partition |  |  |  | 1 | 1 | set | 15500 | 15500
G | TILING WORK
G.1 | Providing and laying tiles in flooring (600 mm x 600 mm x 12 mm) in all colours and shade, laid on 20 mm thick cement mortar 1:4 (1 cement: 4 coarse sand) finished with flush pointing in white cement | [5 empty] | sq.m | 1424.35 |  | GL0002
| New conference hall toilet floor | 2.64 | 1.2 |  |  | 3.17
| Toilet next the GAB on first floor stair case landing right side | 4 | 2.5 |  |  | 10
| Total estimated quantity |  |  |  |  | 13.17 |  |  | 18758.69
G.2 | Providing and fixing tiles in wall in different sizes (600mm x 600 mm x 12mm) in all colours and shade, on 12 mm thick cement mortar 1:3 (1 cement:3 sand) finished with flush-pointing in white cement | [8 empty] | GL0001
| New conference hall toilet walls | 2.64 |  | 1.8 | 2 | 9.5 | sq.m
|  | 1.2 |  | 1.8 | 2 | 4.32 | sq.m
| Toilet next the GAB on first floor stair case landing right side | 4 |  | 1.8 | 2 | 14.4
|  | 2.5 |  | 1.8 | 2 | 9
| Net quantity |  |  |  |  | 37.22 | sq.m | 1276.33 | 47505
H | PLUMBING WORK
H.1 | Providing and fixing Chlorinated Polyvinyl Chloride (CPVC) pipes - class 1 (SDR11), having thermal stability for hot & cold water supply, including all CPVC plain & brass threaded fittings, including fixing the pipe with clamps at 1.00 m spacing. This includes jointing of pipes & fittings with one step CPVC solvent cement and testing of joints complete as per direction of Engineer in Charge. Internal work - Exposed on wall. | [5 empty] | m |  |  | PI0303, PI0304,
H.1.a | 40 mm nomimal outer dia pipes |  |  |  |  | 50 | m | 1123.62 | 56181
H.1.b | 32 mm nomimal outer dia pipes |  |  |  |  | 75 | m | 822.02 | 61651.5
H.2 | Providing and fixing Chlorinated Polyvinyl Chloride (CPVC) pipes - class 1 (SDR11), having thermal stability for hot & cold water supply, including all CPVC plain & brass threaded fittings, i/c fixing the pipe with clamps at 1.00 m spacing. This includes jointing of pipes & fittings with one step CPVC solvent cement and the cost of cutting chases and making good the same including testing of joints complete as per direction of Engineer in Charge. Concealed work, including cutting chases and making the good walls etc. | [7 empty] | 0 | PI0316
H.2.a | 20 mm nomimal outer dia pipes |  |  |  |  | 100 | m | 437.01 | 43701
H.3 | Providing & fixing white vitreous china wash basin, including C.I brackets, 15mm C.P. brass pillar taps, c.p. chain & rubber plug, 32mm pvc waste, 32mm dia. trap & union, repair walls- Flat back wash basin 630x450mm
| New conference hall toilet |  |  |  | 1 | 1 | each | 5088.01 | 5088.01 | PI0087
H.4 | Providing & fixing European-type vitreous china w.c pedestal including seat and lid with c.p brass hinges, 15 lit white vitreous china low level cistern, fittings, brackets, repair walls |  |  |  | 1 | 1 | each | 6295.1 | 6295.1 | PI0050
New conference hall toilet
H.5 | Providing & fixing c.p. brass stop cock - 20mm, standard, c.p knob |  |  |  | 1 | 1 | each | 1217.31 | 1217.31 | PI0186
New conference hall toilet
H.6 | Providing & fixing bevelled edge mirror (superior glass) incl.4mm A.C sheet base fixed to wooden cleats
| 400x450mm (New conference hall toilet) |  |  |  | 1 | 1 | each | 2052.4 | 2052.4 | PI0250
| 2730x730 mm (Gents toilet) |  |  |  | 1 | 1 | each | 11839.58 | 11839.58
H.7 | Providing & fixing toilet paper holder - C.P. brass |  |  |  | 1 | 1 | each | 663.43 | 663.43 | PI0260
New conference hall toilet
H.8 | Providing & fixing soap dish including brackets, wooden cleats, c.p. brass screws |  |  |  | 1 | 1 | each | 549.69 | 549.69 | PI0275
H.9 | Providing & fixing Indian-type vitreous china w.c squatting pan with 10 litres vitreous china cistern including 100 mm P trap, fittings and repairing walls complete |  |  |  | 2 | 2 | each | 5160.33 | 10320.66
H.10 | Providing & fixing P.P (Polypropylene) three layered soil waste pipes, single or double socketed, including pipe clip complete (excluding the cost of P.P fittings)- 110 mm dia |  |  |  |  | 350 | m | 676.5 | 236775 | PO0370
H.11 | Providing & fixing P.V.C vent pipes, single or double socketed, including pipe clip complete (excluding the cost of PVC fittings)- 75 mm dia |  |  |  |  | 120 | m | 384 | 46080
H.12 | Providing & fixing P.P Pipe connector( 100 mm dia) |  |  |  |  | 36 | each | 180.31 | 6491.16
H.13 | Providing & fixing P.P Coupler (110 mm dia) |  |  |  |  | 36 | each | 163.77 | 5895.72
H.14 | Providing & laying H.D.P.E pipes, 10 PN, including H.D.P.E fittings (excluding trenching, refilling & thrust block)160 mm |  |  |  |  | 72.5 | m | 1321.7 | 95823.25 | PO0722
H.15 | Providing & fixing P.P nahani floor trap 110 mm x 75 mm |  |  |  |  | 12 | each | 197.97 | 2375.64 | PO0565
H.16 | Providing & fixing P.P Coupler 75 mm |  |  |  |  | 36 | each | 242.18 | 8718.48
H.17 | Providing & fixing P.P Coupler 110 mm |  |  |  |  | 18 | each | 389.93 | 7018.74
H.18 | Providing & fixing P.P Reducer 110x75 mm |  |  |  |  | 36 | each | 397.7 | 14317.2
H.19 | Providing & fixing P.P plain bend 75 mm |  |  |  |  | 18 | each | 325.78 | 5864.04
H.20 | Providing & fixing P.P plain bend 110 |  |  |  |  | 20 | each | 497.35 | 9947
H.21 | Providing & fixing P.P Single Y, plain, 110 mm dia |  |  |  |  | 22 | each | 925 | 20350
H.22 | Providing & fixing P.P Double Y, with door 110 mm dia |  |  |  |  | 8 | each | 1450 | 11600
H.23 | Providing & fixing P.P single Tee plain, 75 mm dia |  |  |  |  | 12 | each | 415 | 4980
H.24 | Fixing of usable wash basins |  |  |  | 20 | 20 | no. | 1146.42 | 22928.4
H.25 | Fixing of water closets & urinals |  |  |  | 25 | 25 | no. | 2700 | 67500
I | PLASTERING AND PAINTING WORK
I.1 | Providing & laying 12mm cement plaster in C.M 1:3, including providing and mixing water-proofing materials in proportion recommended by the manafacturers | [5 empty] | sq.m | 288.05 |  | PL0020, PL0100
| Service duct 1 & 2 | 2.5 |  | 12.2 | 4 | 122
|  | 1.2 |  | 12.2 | 4 | 58.56
| Service duct no. 3 | 2.5 |  | 7.7 | 2 | 38.5
|  | 1.1 |  | 7.7 | 2 | 16.94
| subtotal |  |  |  |  | 236 | sq.m |  | 67978.97
I.2 | Finishing wall with water-proof cement paint, new work, 3 coats | [6 empty] | 99.27 |  | PT0030
| Service ducts 1,2 & 3 |  |  |  |  | 236 | sq.m |  | 23427.01
I.3 | Providing, preparing and applying Sumdang painting (Not washable), Rab | [5 empty] | sq.m | 986.71 |  | PT0090
| The flag pole base (Bumpa) | 1.5 | 1 |  | 1 | 1.5
| Wall section behind IMS toilet | 4.95 | 1.2 |  | 1 | 5.94
| Estimated quantity |  |  |  |  | 7.44 | sq.m |  | 7341.1224
I.4 | Providing and applying finishing coats Synthetic enamel, for steel & wood work, two coats on new work |  |  |  |  | 2.42 | sq.m | 106.74 | 258.3108
J | ROAD WORKS
| Consolidation of sub-grade with plate compactor, and making good the undulation with earth and re-compacting the sub grade | [5 empty] | sq.m | 10 |  | RW0123
| Road repair works | 72.5 | 0.45 |  |  | 32.625 |  |  | 326.25
| Providing and laying Granular sub-base course (GSB) 220mm to required degree of compaction with proper formation of cross fall using motor grader for laying and compacted to required density as per material gradation and aggregate quality specified | [5 empty] | cu.m | 2192.1 |  | RW0131
| Road repair works | 72.5 | 0.45 | 0.22 |  | 7.18 | cu.m |  | 15739.25
| Providing and laying wet mix macadam graded aggregate base course 100 mm to required degree of compaction with proper formation of cross fall by using well graded crushed aggregates premixed with OMC using suitable mixer, motor grader as per material gradation and aggregates quality specified | [5 empty] | cu.m | 2933.68 |  | RW0131
| Road repair works | 72.5 | 0.45 | 0.1 |  | 3.26 |  |  | 9563.79
| Premix consolidated carpet surfacing including a tack coat @ 0.75 kg bitumen emulsion per sq.m of road surface | [5 empty] | sq.m | 514.5 |  | RW0154
| Road repair works | 72.5 | 0.45 |  |  | 32.63 | sq.m |  | 16788.14
K | ELECTRICAL WORK
K.1 | Wiring for 5/6 pin, 16 ampere plug point with 4 sq.mm 1.1kV grade,PVC insulated copper conductor cable in PVC casing & capping with providing and fixing 5/6 pin, 6/16 ampere socket outlet & switch including earthing the third pin,connections, painting, testing & commissioning etc. as required, Long point | [5 empty] | point | 3264.52 |  | WP0147
| For pressure booster pump |  |  |  | 1 | 1 |  |  | 3264.52
K.2 | Wiring for light and 2 pin light socket outlet with 1.5 sq.mm 1.1kV grade, PVC insulated copper conductor cable inrecessed HDPE pipe including connections, painting, testing and commissioning etc. as required, medium point | [5 empty] | point | 1985.5 |  | WH0301
| New conference hall toilet |  |  |  | 1 | 1 | point |  | 1985.5
K.3 | Supplying & fixing of prewired indoor recessed mounted round/Square LED luminiares of 3000/4000/6000k, complete with all accessories with necessary testing & commissioning & cutting & painting as required. | [5 empty] | each | 864.38 |  | IL0524
| 8W |  |  |  | 1 | 1 |  |  | 864.38
K.4 | Providing, installation, testing and commissioning of pressure booster pump rated at 0.5 hp, with automatic mode of operation, single phase, all accessories complete. Brand Grundfos and equivalent |  |  |  |  | 1 | set | 15000 | 15000
1375348.7254

## Schedule
Sl. No. 1 | Description | Phase of construction
1 | Earthwork, demolishing & dismantling work, surface preparation works, etc. | Phase 1
2 | Outdoor plumbing and sanitary drainage works | Phase 1
3 | Indoor plumbing and sanitary drainage works | Phase 2
4 | Filler materials, skin/surface treatment, plaster, paint, water proofing, etc | Phase 3
5 | Fabrication and partition works, skirting works, etc | Phase 1
6 | Electrical works | Phase 1

## WS,S,IP,CW,EW
Scope of work(s)
Sl. No. | Item Description | Length (m) | Breadth (m) | Height/ depth (m) | Nos. | Quantity | Unit | Estimated Rates | Amount (Nu.) | BSR reference
A | Earthwork, Dismantling & Demolition works
3
4
4 | Consolidation of sub-grade with plate compactor, and making good the undulation with earth and re-compacting the sub grade | [5 empty] | sq.m | 10 |  | RW0123
| Road repair works | 72.5 | 0.45 |  |  | 32.625 |  |  | 326.25
5 | Providing and laying Granular sub-base course (GSB) 220mm to required degree of compaction with proper formation of cross fall using motor grader for laying and compacted to required density as per material gradation and aggregate quality specified | [5 empty] | cu.m | 2192.1 |  | RW0131
| Road repair works | 72.5 | 0.45 | 0.22 |  | 7.18 | cu.m |  | 15739.25
6 | Providing and laying wet mix macadam graded aggregate base course 100 mm to required degree of compaction with proper formation of cross fall by using well graded crushed aggregates premixed with OMC using suitable mixer, motor grader as per material gradation and aggregates quality specified | [5 empty] | cu.m | 2933.68 |  | RW0131
| Road repair works | 72.5 | 0.45 | 0.1 |  | 3.26 |  |  | 9563.79
7 | Premix consolidated carpet surfacing including a tack coat @ 0.75 kg bitumen emulsion per sq.m of road surface | [5 empty] | sq.m | 514.5 |  | RW0154
| Road repair works | 72.5 | 0.45 |  |  | 32.63 | sq.m |  | 16788.14
8
9
10
11
12
13
14
15
16
17
18
19
20
21
24
25
26
27
28
29
30
31
32
33
34
35
36
37
38
39
40
41
42
43
44
45
46
47
48
49
50
51
52
53
54
55
56

## Rate analysis
Total CP | Total Sales | 20% | 80% | Actual
2.2 | 30 | 6 | 24 | 21.8
Income tax |  | 1.8
Net |  | 4.2
|  | 50 | 50
|  | 15 | 15 | 2.2
|  | 4.5 | 12.8 | Profit
10.5
AR1
Mirror |  | Coeff. | Unit | Rate | Amount
LB0033 | Carpenter gd.2 | 0.3214 | day | 800 | 257.12
LB0077 | Labour | 0.29484 | day | 600 | 176.904
MT1631 | Mirror (Bevelled egde) 2.27m x 0.73 m | 1 | each | 9715.2 | 9715.2
Sub-total |  |  |  |  | 10149.224
Constants
5% |  |  |  |  | 507.4612
sub-total |  |  |  |  | 10656.6852
1% |  |  |  |  | 106.5669
sub-total |  |  |  |  | 10763.2521
10% |  |  |  |  | 1076.3252
Estimated rate |  |  |  |  | 11839.5773
AR2=25 (dismantling cpvc pipe and fittings)
DD0075
AR3- Laminated pvc partition boards and frames fixing
Description |  | Coeff. | Unit | Rate | Amount
LB0021 | Carpenter gd.1 | 0.22243 | day | 1000 | 222.43
LB0033 | Carpenter gd.2 | 0.09706 | day | 800 | 77.648
LB0077 | Labour | 0.36532 | day | 600 | 219.192
Sub-total |  |  |  |  | 519.27
Constants
5% |  |  |  |  | 25.9635
sub-total |  |  |  |  | 545.2335
1% |  |  |  |  | 5.4523
sub-total |  |  |  |  | 550.6858
10% |  |  |  |  | 55.0686
Estimated rate for fixing |  |  |  |  | 605.7544

## FieldGround Data
Project: | R & M Bhutan Post GPO/HQ building, Thimphu
Title: | External & Internal plumbing requirment and measurement details
Sl. No | Brief Description | Length(m) | Breadth (m) | Height (m) | Thickness | Nos. | Quantity | Unit | Location | Remarks
| UG sewerage pipe length | 38 | [6 empty] | North side
|  | 34.5 | [6 empty] | South side
|  | 72.5 |  |  |  |  | 72.5 | m
Pipe length in the ducts
| Duct 1 | 10.5 |  |  |  | 6 | 63
| Duct 2 | 10.5 |  |  |  | 6 | 63 | m | HQ main entrance left side | Upto first floor roof level
| Duct 3 | 7 |  |  |  | 6 | 42
| Gents toilet | [7 empty] | 1st Floor
| Floor area | 5.6 | 4.2 |  |  |  | 23.52 | sq.m
| additional | 1.38 | 2.47 |  |  |  | 3.41 | sq.m
[7 empty] | 26.93 | sq.m
Ladies Toilet
| Floor area | 5.5 | 4.46 |  |  |  | 24.53
| deduction | 1.93 | 0.77 |  |  |  | 1.49
[7 empty] | 23.04 | sq.m | 1st Floor
| Overhead tank (ht) in meter | 9.5 | [5 empty] | m | Upper parking (Reference level RL2) | RL2 to OHT tower top slab
|  | 6.35 | [5 empty] | m | Upper parking (Reference level RL2) | RL2 to OHT tower mid tanks
Ground level difference
| Ground level 2 (RL2) | 3 | [5 empty] | m | HQ office and Postal museum location to ground floor (GPO floor level)
| OHT to GL2 (RL2) | 12.5 | [5 empty] | m
Hydraulic Gradient for water supply line
| Head (meters) | H max (m) | H min (m)
|  | 12.5 | 1.73 |  | 0.5 to 1 hp single phase auto pressure booster pump installation to be included after pipe pressure sizing
Raidal and Dead end type water supply layout
| Ground Floor toilets | Wash basin | Wash closet | Urinal |  |  | 3
| PMT | 1 | 2 |  |  |  | 1
| GPOT | 3.05 | 2.9 |  |  |  | 1
| IMST | [5 empty] | 1
| First floor toilets | GAB area+Ladies+philately+IAU+Gents toilets |  |  |  |  | 6 |  | inclusive new conference toilet
| GABT | [5 empty] | 1
| LT | [5 empty] | 1
| GT | [5 empty] | 1
| PT | [5 empty] | 1
| IAUT | [5 empty] | 1
| Ctnew | [5 empty] | 1
| 2nd Floor toilets | CEO's chamber and PA area toilets |  |  |  |  | 3
| CEOT | [5 empty] | 1
| PAT | [5 empty] | 2
| Total toilets | [5 empty] | 12
Water Supply fixture Units (WSFU) as per IPC table 103.3(2)
| Fixtures | Occupancy | Quantity | Load values | Total
| Water closet | Private | 19 | 2.2 | 41.8
| Wash basin | Private | 14 | 2.25 | 31.5
| Urinal | Private | 4 | 3 | 12
| Faucets | Private | 12 | 1 | 12
[5 empty] | 97.3 | Approx. 100
| Water Flow determination | IPC table 103.3(3)
| WSFU = 100 | Gallons per minute | cubic ft per minute | Liter per minute
|  | 43.5 | 5.82 | 164.8
| Sand bedding | 7.5 cm compacted sand bedding
upto 20 cm from base of pipe
| Filter materials | 100 to 200 mm stones
| Sanitary Drainage | Min | Max | Unit | Conversion coefficient | Min | Max | Unit | Remarks
| Horizontal drains and building drains |  | 100 | ft | 0.3048 |  | 30.48 | m
| Man hole location interval |  | 400 | ft | 0.3048 |  | 122 | m
| Stone soling | 100 | 225 | mm |  |  |  |  | 25mm tolerance
| Road gradient |  | 10% | [5 empty] | For design speed of 30km/hr
| Sewerage pipe size (max) connecting to the municipal sewerage size |  | 160 | mm
| Building height ground level (RF2) to roof top level |  | 38.5 | ft | 0.3048 |  | 11.73 | m | Ground level 2 to roof top level
| Building height ground level (RF2) to 2nd floor level |  | 25.5 | ft | 0.3048 |  | 7.77 | m
| Building height ground level(RF1 to RF2) | [5 empty] | 12.2
| Description | Value | Unit | Value | Unit | Code Section |  | Remarks
1 | Total water supply fixture units | 97.3 | WSFU |  |  | E103.3(2)
2 | Convert WSFU to GPM | 43.5 | GPM | 164.8 | L/m | Table E201.1
3 | Minimum water pressure available from overhead tank | 2.46 | PSI | 16.96 | kPA
Overhead tank top slab level to RL2 (upper parking level)
4 | Pressure loss- due to building height ( 0.433 psi/ft) or (9.81 kPA/m) |  |  | 75.537 | kPA
5 | Minimum water pressure required at remote fixture |  |  | 20 | kPA | IPC table 604.3
6 | Pressure loss through RPBF (backflow preventer) | 4 | PSI | 28 | kPA
7 | Pressure loss through PRV (pressure regulating valve) | 0 |  | 0 |  |  | Not required as min. pressure is below 80 PSI
8 | Total pressure required for operation (4 to 7) | 4 |  | 123.537 | kPA
9 | Pressure available for friction loss (3 minus 8) | 15.45 | PSI | -106.577 | kPA
10 | Total development length of piping (main to remote fixture) | 221.45 | ft | 67.5 | m
11 | Multiply total pipe length by 1.5 (provision for fittings and valves) | 332.175 | ft | 101.25 | m
12 | Friction loss per 100 ft of pipe length | 7.36 | psi/100 |  |  |  | E 103.3(6)
13 | Main pipe size | 1 1/2 | inches | 38 | mm |  | E103.3(3)
| Therefore, select main pipe size |  |  | 40 | mm
Brief Scope of work
1 | Sanitary Drainage | Min | Max | Unit | Conversion coefficient | Min | Max | Unit | Remarks
| Horizontal drains and building drains |  | 100 | ft | 0.3048 |  | 30.48 | m
| Man hole location interval |  | 400 | ft | 0.3048 |  | 122 | m
2 | Sewerage pipe size (max) connecting to the municipal sewerage size |  | 160 | mm
3 | Building height ground level (RF2) to roof top level |  | 50.5 | ft | 0.3048 |  | 15.39 | m | Ground level 2 to roof top level
| Building height ground level (RF2) to 2nd floor level |  | 25.5 | ft | 0.3048 |  | 7.77 | m

## 2 new chambers divisional heads
Finance mini conference room
Description | Length (m) | Breadth (m) | Height (m) | Location | Remarks
Whole Room | 5.05 | 3.05 | 3.12 | Between Finance Division and Finance Head | The room is to be divided in two chambers for HoDs, Finance Head and AHRD head
Divided rooms | 2.02 | 3.05 | 3.12
Material Options
Partition works | Aluminium and laminated board (corporate color/neutral color)